Request for Tender for Supply and installation of a Site Surface Water Upgrade System at SmartPly Europe DAC

Contents

Disclaimer	2

1.	Introduction	3

2. 	Scope of Works	3

2.1	Project Timelines	6

2.2	Location -	6

2.3 	Site Visit	7

2.4	Minimum Requirements	7

3.	Award Criteria	8

4.	Tender Validity Period	9

5.	Confidentiality of Evaluation	9

6.	Qualifications	10

8.	Determination of Responsiveness	10

9.	Tender Clarification	10

10.	 Modification of the Request for Tenders/Supplemental Information	10

11.	 Contract Obligations	11

12.	Form of Tender	11

13.	Tender Bid	11

14.	Payments/Invoicing	11

15.	Pricing	12

16.	Presentation of Tender	12

APPENDIX  1. Form of Tender	13

APPENDIX 2. Questionnaire	15

APPENDIX 3. PRICING SCHEDULE & AWARD CRITERIA	23

APPENDIX 4. Drawings and calculations	30

“Tender Submission for the above Tender and should be delivered no later than 12:00 hrs on 29th of October 2021”

# Disclaimer

This document issued herewith is for information only and does not constitute, and shall not be interpreted as, an offer for sale, prospectus, or the basis of a contract.

Candidates are recommended to read the documents thoroughly.  While all reasonable steps have been taken to ensure that the information set out in the documents is accurate and up to date, no representation or warranty, express or implied, is or will be made or given in relation to the accuracy or the completeness of any information contained in the documents or otherwise provided by or on behalf of SmartPly (in writing or otherwise) to any interested party or its advisers. No responsibility or liability for any loss or damage arising as a result of reliance on these documents, or for the information contained in these documents or for any omission is or will be accepted by SmartPly or by any of its officers, employees, agents or professional advisers.  No officer, employee, agent, or professional adviser of the company has any authority to give or make any representation or warranty, express or implied, in relation to such information. SmartPly officers, employees, agents and professional advisers expressly disclaim any and all liability arising out of such documentation or information and any errors or omissions in or from the documents and information.

SmartPly reserves the right to discontinue the procurement process at any time.

Please note that information relating to this Questionnaire, including clarifications and changes, will be published on the Irish Government Procurement Opportunities Portal (www.etenders.gov.ie). Registration is free of charge and there is no charge for documents. Please note that SmartPly cannot accept responsibility for information relayed (or not relayed) via third parties.

## 1.	Introduction

SmartPly Europe DAC is situated at Belview Port, near Waterford city and has produced Oriented Strand Board (OSB) since 1996 for a range of structural applications including flooring, wall sheathing, roofing, hoarding, furniture and packaging. OSB is a strong, durable wood panel which is increasingly used throughout Europe in the Offsite construction sector. It is manufactured by compressing precisely engineered strands of wood with gluing resins at high temperature to create a strong and versatile panel. It is an innovative, environmentally sustainable timber-based solution for structural and non-structural building applications. SmartPly are a leading supplier of premium OSB products in Europe.

## 2. 	Scope of Works

SmartPly Europe DAC are requesting tender proposals for site surface water installation upgrades. The aim is to ultimately improve its current site surface water quality collection system and to ensure that it will be suitable for the proposed expansion of the site to 30ha. Smartply have engaged with WEW Consulting Engineers to look at design proposals for this project and these documents are available for your perusal. The successful contractor will be requested to supply and install the upgrades into 3 distinct sections as outlined in the attached schematics. There is scope in this tender proposal to include value engineering (VE) i.e., redesigning aspects to enhance performance and possibly reduce cost. Any VE proposals will have to be clearly identified and explained in the tender proposal package.

The surface water upgrades will consist of three different installations:

- Settling tank inlet splitter arrangement (drawing 383-403)

- Inlet pit screen (drawing 383-404)

- Floating decanter (drawing 383-405)

- Settling tank inlet splitter arrangement

To facilitate a consistent flow of 5-20m3/hr through one of the settling tanks at a given time, this splitter arrangement has been designed. The concept relies on the size of the slot and the height of the interchangeable hand stops.

The 50x90mm slot will allow approximately 11m3/hr to pass through to the “Duty” settling tank. The adjustable plate should allow the slot size to be reduced to 50x50mm. If the upstream flow is greater than 11m3/hr, the water level will rise above 270mm and start to flow into the “Standby” settling tank. This overflow is designed to facilitate flows of approximately 300m3/hr. This will increase the depth of water upstream and therefore the flow through the 50x90mm slot will increase to approximately 20m3/hr. Flows greater than this are considered storm flows and will overflow both weirs.

For the design to work as outlined the taller hand stop with the slot must be 400mm high from the bottom of the chamber with a 50x90mm slot at the bottom. The other hand stop must be 270mm and form a good seal at the bottom of the chamber. Both hand stops must be at least 1m wide.

The hand stop must be removable and interchangeable to allow the operator to change which setting tank is the duty tank.

The drawing is based on HDPE hand stops supplied by Waterfront Fluid Controls Ltd. Other suppliers are acceptable. 2No handles would be preferred. The height of the handle should be below the existing grid of the chamber.

Anchor bolts and waterproof sealant are suitable to attach the mounting set, frame, and dividing wall to the concrete chamber. All wetted materials shall be Stainless Steel 304 or resistant to rust.

- Inlet pit screen

To aid in removing solids from the surface water network it is proposed to install a below ground screen upstream of Silt Trap 3.

The concept is to divert flow from the existing surface water drain, through a 3mm wedgewire screen and then allow the screen water to flow back to the existing surface water drain. The screen pit is designed to be emptied by a mini wheel loader with digging attachment, mini digger or back actor on a digger with a grading bucket.

The yard area where the screen will be located is hardcore and slopes down to the existing concrete drain. Excavations and new concrete will be required to tie in the 2No 300mm pipes to the drain. The client has plans to pour a new concrete slab on this yard area and the client will advise whether this larger slab forms part of these works or not.

A 300mm tall, stainless-steel weir shall be fitted to the existing drain to divert flow to the pit screen.

The screen shall be a flat, stainless steel, wedgewire screen, with a 34SB profile (or similar) and 3mm slot size. A protective frame shall be included on all 4 sides. The screen shall be removable so a slot shall be constructed on 3No sides of the pit screen using stainless steel 50mm angle or similar. The screen shall be fitted with 2No handles on the top for removal. Hall Pyke supply custom wedgewire screen as described, other suppliers are acceptable.

Steps shall be included on the clean water side of the screen for access. A safety handrail shall be included.

- Floating decanter

The purpose of the floating decanter is to continuously discharge surface water from the duty setting tank at a rate equal to the inlet flow. The existing overflow weir can do this but due to the nature of the business onsite, fine woody material ends up in the settling tank and can float over the weir. The decanter should be designed to discharge water 500mm below the surface and should not discharge water from the bottom 700mm as this will contain settled solids.

The drawing provided shows a decanter supplied by EWFM as their standard offering. Other suppliers are acceptable. As part of these works 2No decanters will be installed one for each settling pond.

The pipe size shall be DN 150, material requirements shall be stainless steel, flowrate shall be <50m3/hr. The dimensions of the settling tank are approximately 30m x 40m with sloped sides. The max liquid level is 3.2m, minimum liquid level shall be ~700mm and distance between liquid level and decanter inlet shall be at least 500mm and not more than 750mm.

The decanter will be fitted to newly installed DN150 PN16 SS pipework. The existing pipework could not be survey extensively, however it appears to be 150mm PVC. The pipe work should be assumed to be broken at the wall of the tank. The current proposal shown in the drawing is to remove enough concrete (assume 1000mmx1000mm) to expose a suitable section of the 150mm pipe to allow a Viking Johnson (VJ) coupling to be installed. The VJ shall connect the existing PVC pipe to new SS pipework. The VJ shall then be cast in concrete (assume 1m3).

The DN150 pipework shall include 2No SS gate valves with extended handles to allow operation from the existing walkway. Universal joints and supports may be necessary. One valve will be located on a tee piece to act as the low-level outlet when the tank needs to be drained. The second will be used for flow control and isolation of the decanter outlet. SS pipe supports may be attached to the floor of the settling tank with anchor bolts.

The offers will include all provision, supply, installation and commissioning of these upgrades.

If you have any issues relating to the specification, please contact Federico Mento (Environmental Manager) on 051-851233.

## 2.1	Project Timelines

·         Tender issue by 05th October 2021

·         Tender delivered by 29th October 2021

·         Contract Awarded by 5th November 2021

·         Works commencement: December 2021

·         Completion & Handover by May 2022.

## 2.2	Location -

SmartPly Europe DAC., Gorteens, Belview Port, Co. Waterford X91 PX75

## 2.3 	Site Visit

It is advised that you visit the site so you clearly understand the scope and nature of the work as no claim will be entertained in respect of inadequate knowledge of site conditions or scope of work.

Please contact Federico Mento (Environmental Manager) federico.mento@mdfosb.com to arrange a visit to view the installation area and clarify any matters pertinent to your offer.

Please note that the sites operate 24/7 and access and egress via the works area will be required. Phasing of the works may be required. This is to ensure that there is no impact on the day to day operations within the plant.

Please note that Full PPE is required during site visit. (See below list of minimum required PPE).

## 2.4	Minimum Requirements

Only those tenderers who demonstrate that they meet the following minimum criteria will be

considered;

- Tenderers must conform to SmartPly’s Contractor Safety Requirements

- Tenderers must provide figures on turnover demonstrating sound financial standing and must be capable of providing Smartply with a letter from their Banker reflecting a sound business, if requested.

- Tenderers must demonstrate adequate previous experience of delivering a similar type and scale of contract.

- Tenderers must complete the Contractor Safety Assessment Form

- Tenderers must complete all information required in the award criteria

- All Tenderer’s must sign and return the Form of Tender attached (Appendix 3).

- Tenderers must comply with all requirements as laid out in the following, Safety, Health and

Welfare at Work Acts;

- Safety, Health and Welfare at Work, 2005

- General Application Regulations, 2007

- Construction Regulations, 2013

- Human Trafficking) (Amendment) Act 2013

## 3.	Award Criteria

The successful contractor will be selected based on the Award Criteria below.

Tenders will be evaluated on this basis and there is a requirement to comply with all aspects listed, irrespective of pricing considerations. Please provide and demonstrate clearly your compliance with the award criteria. The decision of Smartplty thereon shall be final.

| Tender for Site Surface Water Installation Upgrades at SmartPly Europe DAC Selection Criteria, Rules & Weightings |
| --- |
| REF | PASS/FAIL CRITERIA | PASS REQUIREMENT |
| A1 | Candidate Summary | Candidates must answer this section. If the candidate is a grouping, then a separate questionnaire must be completed for each group member. |
| A2 | Financial Capacity | Candidates must provide details of their turnover in respect of the previous two financial years. Alternatively, candidates must safisfy SmartPly that they have adequate financial capacity to deliver the services by alternative means. NOTE: in the case of the candidate being a grouping, this condition may be satisfied by the group members as a whole. |
| A3 | Insurances | Candidates must provide a statement from their insurers confirming that the candidate currently has in place the stated minimum levels of insurances, or that such levels can be obtained if successful in the competition. |
| A4 | Declaration of Bona Fides | Candidates must complete, sign and date this Declaration. Non-compliant candidates under any of the headings will be automatically disqualified. |
| A5 | Tax Clearance Certificate | Please provide evidence of a current and valid tax clearance certificate. |
| REF | WEIGHTED CRITERIA | MAX POINTS AVAILABLE | MINIMUM RULE / ELIMINATOR | MIN POINTS REQUIRED |
| B1 | Ultimate Price | 6,000 | Candidates must provide a completed fixed cost-effective proposal, As per Appendix 3 | N/A |
| B2 | Previous Experience | 2,000 | Candidates must provide details of at least 3 successfully executed projects of similar nature, scale and complexity to those to be carried out under this scope of works. | 1,200 |
| B3 | Project Plan | 1,000 | Provision of Programme of work highlighting all Milestones in MS Project or similar. Installation schedule with manning levels – all resources identified and quantified | 600 |
| B4 | Health and Safety (Policy and Procedures) | 1,000 | Candidates must have undertaken a course introducing the principles of the Safety, Health and Welfare at Work (Construction) Regulation’s amendment 2019 with regard to the service provider’s duties under those Regulations. Candidates must complete section B4 fully. | 800 |
| TOTAL | 10,000 |  |  |

Tenders will be evaluated based on the above award criteria and there is a requirement to comply with all aspects listed, irrespective of pricing considerations.  The decision of Smartply thereon shall be final.

SmartPly reserves the right to suspend and/or terminate the contract in the event of consistently poor performance (as found by Smartply) or in the event of a breach of its terms and conditions of purchase. In addition, Smartply reserves the right to request beast and final offers “BAFO”.

## 4.	Tender Validity Period

To allow sufficient time for tender assessment a Tender Validity period of 90 days is required, this period commencing on the closing date by which the tenders are to be returned.

## 5.	Confidentiality of Evaluation

After the official opening of Tenders, information relating to the examination, clarification, evaluation, comparison of Tenders and recommendations concerning the Award of Contract will not be disclosed to Tenderers or other persons not officially concerned with such process until the Award of Contract to the successful Tenderer has been announced in conformity with national law.

The distribution of this Tender Document is for the sole purpose of obtaining Tenders as referred to therein. The distribution does not grant permission or licence to use the documents for any other purpose.

Tenderers are required to treat the details of all documents supplied in connection with the tender process as private and confidential. Similarly, the Client undertakes to use its reasonable endeavours not to disclose to third parties any confidential information received from Tenderers, subject to its obligations under law.

Any effort by the Tenderer to influence any member of Smartply staff in the process of examination, clarification, evaluation and comparison of Tenders and in decisions concerning the Award of Contract may result in the rejection of that Tender.

## 6.	Qualifications

The Tenderer shall submit a clean unqualified tender.

If any qualified tenders are received, the Tenderers will be requested to withdraw qualifications.      In the event that the Tenderer fails to withdraw a qualification, the tender will be considered invalid and Smartply will not assess the tender.

7.	Disclosing Tenders

Acceptance of tender documents by a Tenderer shall be held to imply a guarantee that the amount of the tender will not be disclosed by the Tenderer to any person or body prior to the lodgement of the tender and a wholly bona fide tender will be submitted.

## 8.	Determination of Responsiveness

After the official opening of Tenders, the Purchaser will determine whether each tender is substantially responsive to the requirements of the tender documents.  If a material deviation exists that limits in any substantial way the Purchaser’s rights or the Tenderer’s obligations under the Contract, the tender shall be rejected.

## 9.	Tender Clarification

If you have any Queries or Clarifications regarding this process or the documentation supplied by Smartply please address all communications in writing to John.Browne@mdfosb.com Tender queries submitted in any other manner will be disregarded.  Such queries as well as clarifications will be communicated to all Tenderers, without revealing the identity of the questioning entity. The closing date for queries will be five (5) days before the return date for tenders.

To assist in the examination and comparison of tenders, the purchaser may ask the Tenderer for Clarification of their tenders, including breakdown of unit prices.  Tenderers may be requested to attend on site for a brief meeting and to present their tender proposals.

## 10.	 Modification of the Request for Tenders/Supplemental Information

Smartply reserve the right to update, delete, vary, extend or alter this Request for Tender and the information and documents contained herein.

Any advice of a modification to the Request for Tender shall be issued at least five (5) days before the Tender Deadline and shall be used as an addendum to, and shall be deemed to constitute part of, the Request for Tenders. If necessary, Smartply shall revise the Tender Deadline in order to comply with requirement.

## 11.	 Contract Obligations

The successful Tenderer will be obliged to;

- Comply with the terms of Circular 43/2006 Tax Clearance procedures

- Comply with obligations relating to employment protection and working conditions. Please consult government website http://www.employmentrights.ie/. For details.

- Comply with current Health & Safety legislation.

- Comply with terms and conditions of contract which will be issued to the successful candidate.

## 12.	Form of Tender

The Form of Tender is an acknowledgement by the Tenderer that this Invitation to Tender, enclosed Conditions of Contract and contents therein are understood in full. The Form of Tender must be signed and returned with quotations submitted based on tender response document attached.

## 13.	Tender Bid

- Prices should be quoted in Euro (€) and should be exclusive of VAT

- Prices should include all consignment stock costs (if applicable)

- No hidden or additional costs should apply

- Prices should remain valid for the full contract period stated

- Please enter your price in Appendix 3

## 14.	Payments/Invoicing

SmartPly operates in accordance with the European Communities (Late Payment in Commercial Transactions) regulations 2002.

Invoices should be forwarded to our accounts department, with a COPY to the Project Manager at the following addresses:

Accounts Dept.

SmartPly

Belview,

Slieverue,

Waterford.

Please note that our payment terms are 30 days from receipt of invoice.

## 15.	Pricing

Pricing must include all costs associated with providing the services to Smartply as outlined in appendix 3, including all expenses associated with attendance at site meetings etc

## 16.	Presentation of Tender

The number of copies of completed Tender documents required is three. Size should be A4 only.

The Tenderer is fully responsible for the safe and timely delivery of the tender.

Any evidence of suspected collusion in tendering will be brought to the attention of the Competition Authority for investigation in conjunction with the Competition Act 2002.

The Tenderer is fully responsible for the safe and timely delivery of the tender prior to the closing deadline date. Failure to upload the tender bid within the allocated time frame will not be accepted thereafter.

Tenders received after the closing date and time will not be considered. All tender submission must be uploaded into the etenders website.

The deadline date for tender submissions is Thursday the 29th of October 2021

### APPENDIX  1. Form of Tender

To: SmartPly

We ________________________________________________ the undersigned (hereinafter styled the Contractor(s)), hereby engage to provide and deliver to Smartply at the prices stated, any or all of the commodities/services of the description specified for which this Tender may be accepted, in such quantities and at such times as may be demanded by SmartPly or an authorised officer acting on its behalf in accordance with the attached “Invitation to Tender, Specifications and Conditions of Contract”.

In the case of a limited company, the seal of the company should be affixed to this Form of Tender.

I accept the rules of the tender competition, including:

- Smartply may accept or reject any tender and is not bound to accept the lowest, or any tender it receives.

- Tenders will be evaluated in accordance with the award criteria specified.

- Smartply reserves the right to award separate contracts.

- Smartply reserves the right to seek a best and final offer.

- Non-compliance with the terms and conditions of contract as stated in this tender document may result in the termination of said contract.

- Tenderers’ tax clearance certificates must be kept current at all times.

- Smartply is not responsible for any expense incurred in the preparation or delivery of proposals.

- I/we further declare that we are familiar with the work on offer and have read and understand the Instructions to Tenderer and Bidding Schedule form.

Dated :- ______________ day of  _______________ 2020

| Signature of Tenderer |  |  |
| --- | --- | --- |
| Name of Company |  |  |
| Full Postal Address: |  |  |
| Phone Number: |  |  |
| Fax Number: |  |  |
| Email (if available): |  |  |
| Company Registration Number: |  |  |

### APPENDIX 2. Questionnaire

SECTION A - PASS/FAIL CRITERIA

NB. Without prejudice to the principle of equal treatment, SmartPly is not obliged to engage in a clarification process in respect of questionnaires with missing or incomplete information. Therefore, candidates are advised to ensure that they return FULLY COMPLETED questionnaires in order to avoid the risk of elimination from the competition.

| SUMMARY CONTACT |
| --- |
| Candidate’s Name |  |
| Contact Name |  |
| Position |  |
| Date of establishment |  |
| Legal Status (if any) (Company (Ltd.), Partnership, Sole Trader, etc.) |  |

Is the Candidate a group of economic operators?				Yes/No

If Yes, please provide the following information:

| Please enclose an organisational chart with the proposed hierarchical structure of the grouping including any sub-contractor arrangements | Confirm if attached yes/no |
| --- | --- |
| If your answer is “Yes”, please provide the following information: | Name | Portion to be delivered | Separate Questionnaire enclosed? |
|  | 1. |  |  |
|  | 2. |  |  |
|  | 3. |  |  |
| If you answered ‘No’ above, state number of years actively trading under present name: |  |

NB. Without prejudice to the principle of equal treatment, the contracting authority is not obliged to engage in a clarification process in respect of questionnaires with missing or incomplete information. Therefore, candidates are advised to ensure that they return FULLY COMPLETED questionnaires in order to avoid the risk of elimination from the competition.

Please provide details of turnover for your organisation in respect of the past three financial years or alternatively, if the date of establishment was more recent, information on turnover available on a pro-rata basis.

|  | 2020 | 2019 |
| --- | --- | --- |
| Turnover (€) | € | € |

(i) 	Please submit objective evidence to verify this information either by a statement from your auditor or by means of any other relevant and appropriate documentation available to you.

| Evidence of Turnover |
| --- |
| Tick if attached |  |
| Appendix Number |  |

(ii) 	If a candidate is unable to provide the objective evidence required under (i) above, they must provide evidence of financial capacity for the required services to be demonstrated by any means available to the candidate.

| Evidence of Financial Capacity |
| --- |
| Tick if attached |  |
| Appendix Number |  |

(iii) 	Alternatively, candidates may elect to submit a self-declaration of their financial capacity in the form provided below. However, it is stressed that the contracting authority will satisfy itself of the financial capacity of candidates before deciding on the list of participants to the tender process. Therefore, if a self-declaration is submitted, the relevant evidence required under sections (i) or (ii) above must be submitted promptly on request by the contracting authority.

SELF DECLARATION FORM OF FINANCIAL CAPACITY

Contracting 	SmartPly Europe DAC

Authority:

Competition: 	Tender for Site Surface Water Installation Upgrades at SmartPly Europe DAC

From: 			__________________________

I/We declare that as an applicant interested in being assessed for suitability for this competition, I/we have the financial capacity to meet the minimum standards of Selection Criterion A2 Financial Capacity set down in the Qualification Questionnaire.

Furthermore, I/we will provide the required evidence to support this declaration when requested to do so prior to any decision by the contracting authority on the list of participants for the Tendering process.

This declaration must be signed by your Financial Director.

| SIGNATURE |  | Date |  |
| --- | --- | --- | --- |
| Name |  | Position |  |
| Telephone |  | Email |  |

NB. Without prejudice to the principle of equal treatment, the contracting authority is not obliged to engage in a clarification process in respect of questionnaires with missing or incomplete information. Therefore, candidates are advised to ensure that they return FULLY COMPLETED questionnaires in order to avoid the risk of elimination from the competition.

i) 		Candidates must provide a statement from their insurance company or broker confirming that the candidate currently has in place the stated minimum levels of insurances,

| Insurance | Required Level | Evidence of matching levels attached (Appendix No) |
| --- | --- | --- |
| Public Liability | €2.6M (any one accident) |  |
| Employers Liability | €13M (any one accident) |  |
| Professional Indemnity | €2.6M |  |

ii) 		Alternatively, candidates must provide a statement from their insurance company or broker confirming that the required levels of insurance will be put in place if the candidate is awarded the contract.

| Insurance | Current Level | Evidence of current levels and confirmation of attainability if awarded the contract (Appendix No) |
| --- | --- | --- |
| Public Liability |  |  |
| Employers Liability |  |  |
| Professional Indemnity |  |  |

iii)	 Alternatively, candidates may elect to submit a self-declaration concerning insurance levels in the form provided below, which confirms either a) the possession of the requisite levels of insurance or b) the fact that the required forms and levels of insurance will be attained prior to the award of contract.

It is stressed that if a self-declaration is submitted concerning insurances, the relevant evidence required must be submitted promptly on request by the contracting authority.

SELF DECLARATION FORM OF INSURANCES

Contracting 		SmartPly Europe DAC

Authority:

Competition: 	Tender for Site Surface Water Installation Upgrades at SmartPly Europe DAC

From:       __________________________

Note: Please complete either (A) or (B) below:

(A) 	I/we declare that as an applicant interested in being assessed for suitability for this competition, I/we have the levels of insurances in place to meet the minimum standards of Selection Criterion A3 Insurances set down in the Qualification Questionnaire. Furthermore, I/we will provide the required evidence to support this declaration when requested to do so by the contracting authority prior to any decision by the contracting authority on the list of participants for the Tendering process:

or

(B) 	I/we confirm that, if successful, I/we will be in a position to put the required form and levels of insurances to meet the minimum standards of Selection Criterion A3 Insurances set down in the Qualification Questionnaire. In this regard, I/we confirm that a letter from an Insurance Broker attesting to the fact that, subject to success in this competition, the required levels could be put in place will be provided on request from the contracting authority.

This declaration must be signed by a duly authorised officer.

| SIGNATURE |  | Date |  |
| --- | --- | --- | --- |
| Name |  | Position |  |
| Telephone |  | Email |  |

| Name of Candidate: |  |
| --- | --- |
| Address: |  |

Please tick Yes or No as appropriate to the following statements relating to the current status of your organisation.

| No. | QUESTION | YES | NO |
| --- | --- | --- | --- |
|  |  | Please ( |
| 1. | The Candidate is bankrupt or is being wound up or its affairs are being administered by the court or has entered into an arrangement with creditors or has suspended business activities or is in any analogous situation arising from a similar procedure under national laws and regulations. |  |  |
| 2. | The Candidate is the subject of proceedings for a declaration of bankruptcy, for an order for compulsory winding up or administration by the court or for an arrangement with creditors or of any other similar proceedings under national laws and regulations. |  |  |
| 3. | The Candidate, a Director or Partner, has been convicted of an offence concerning his professional conduct by a judgement which has the force of res judicata or been guilty of grave professional misconduct in the course of their business. |  |  |
| 4. | The Candidate has not fulfilled its obligations relating to the payment of taxes and/or social security contributions in Ireland or any other State in which the tenderer is located. |  |  |
| 5. | The Candidate, a Director or Partner has been found guilty of fraud. |  |  |
| 6. | The Candidate, a Director or Partner has been found guilty of money laundering. |  |  |
| 7. | The Candidate, a Director or Partner has been found guilty of corruption. |  |  |
| 8. | The Candidate, a Director or Partner has been convicted of being a member of a criminal organisation. |  |  |
| 9. | The Candidate has been guilty of serious misrepresentation in providing information to a public buying agency. |  |  |

THIS FORM MUST BE COMPLETED AND SIGNED BY A DULY AUTHORISED OFFICER OF THE CANDIDATE’S ORGANISATION

I certify that the information provided above is accurate and complete to the best of my knowledge and belief.  I understand that the provision of inaccurate or misleading information in this declaration may lead to my organisation being excluded from participation in this and future tenders.

| SIGNATURE |  | Date |  |
| --- | --- | --- | --- |
| Name |  | Position |  |
| Telephone |  | Email |  |

NB. Without prejudice to the principle of equal treatment, the contracting authority is not obliged to engage in a clarification process in respect of questionnaires with missing or incomplete information. Therefore, candidates are advised to ensure that they return FULLY COMPLETED questionnaires in order to avoid the risk of elimination from the competition.

- Provide a current valid tax clearance certificate from the Irish Revenue Commissioners.

| TCC |
| --- |
| Tick if attached |  |
| Appendix Number |  |

- Alternatively, candidates may elect to submit a self-declaration concerning tax clearance in the form provided below, which confirms either a) the possession of a current and valid Tax Clearance Certificate or b) the fact that a Tax Clearance Certificate has been applied for and will be made available upon request.

It is stressed that if a self-declaration is submitted concerning tax clearance, the relevant evidence required must be submitted promptly on request by the contracting authority.

SELF DECLARATION TAX CLEARANCE

Contracting 		SmartPly Europe DAC

Authority:

Competition: 	Tender for Site Surface Water Installation Upgrades at SmartPly Europe DAC

From: 			__________________________

Note: Please complete either (A) or (B) below:

(A) I/we declare that as an applicant interested in being assessed for suitability for this competition, I/we have a current and valid Tax Clearance Certificate in place and our tax affairs are in order. In this regard, our Registration Number and Certificate Number are as follows:

| Registration Number (as shown on Tax Clearance Certificate) |  |
| --- | --- |
| Certificate Number (as shown on your Tax Clearance Certificate) |  |

Additionally, I/we hereby grant the contracting authority permission to verify tax clearance status through Revenue’s online facility (https://www.revenue.ie/itp.view.jsp).

(B) I/we confirm that a Tax Clearance Certificate has been applied for and will be made available promptly upon request from the contracting authority.

This declaration must be signed by a duly authorised officer.

| SIGNATURE |  | Date |  |
| --- | --- | --- | --- |
| Name |  | Position |  |
| Telephone |  | Email |  |

## APPENDIX 3. PRICING SCHEDULE & AWARD CRITERIA

All Works to be carried out as per Smartply DAC Scope of Work,

See attached specification documents

| Pricing Items | Pricing Description | Total Cost € |
| --- | --- | --- |
| 1. | Settling tank inlet splitter arrangement |  |
| 2. | Inlet pit screen |  |
| 3. | Floating decanter |  |
| 4. |  |  |
|  | Total Cost |  |

| Contractor name: |  | Name (print): |  |
| --- | --- | --- | --- |
| Date: |  | Signature: |  |

Please note that Smartply Europe DAC is exempt and that all Quotes and Invoices are to be issued at 0% VAT

NB. Without prejudice to the principle of equal treatment, SmartPly is not obliged to engage in a clarification process in respect of questionnaires with missing or incomplete information. Therefore, candidates are advised to ensure that they return FULLY COMPLETED questionnaires in order to avoid the risk of elimination from the competition.

The contracts listed must demonstrate your skills, efficiency, experience and reliability in respect of the provision of supplies similar to those constituting the subject matter of this contract.

All fields should be completed in full. In the event that the information requested on the value of contracts or identity of clients is considered confidential, candidates must ensure that they provide sufficient information to allow the contracting entity to judge the similarity of these contracts to the services required by SmartPly.

Candidates may submit a maximum of 3 projects only.

| Client | Description of service/product provided | Scale or Approx. value (€) | Contract period |
| --- | --- | --- | --- |

Additionally, candidates are required to provide the contact details of two referees in a\ position to attest to the successful delivery of the contracts listed.

Referee/Reference 1:

Name:  ________________________________

Organisation: ____________________

Address:	________________________________________________________

Telephone: __________

E-mail Address: _________________________________

Referee/Reference 2:

Name:	_______________________________

Organisation: ____________________

Address: _______________________________________________________________

Telephone: ___________

E-mail Address_________________________________

Candidates must provide the information regarding manpower levels on the table below.

Note 1: the purpose of this section is to identify whether the candidate firm has at its disposal the appropriate number of suitably qualified and experienced human resources. Candidates are reminded that they may rely on the resources of other entities on condition that they are fully described and can prove that they will have these resources at their disposal when required.

Note 2: it is emphasised that, at this stage, candidates are not being asked to propose the specific personnel for the delivery of the contract.

Please state the total number of persons directly employed by you over the past 3 years.

|  | 2020 | 2019 | 2018 |
| --- | --- | --- | --- |
| Permanent |  |  |  |
| Temporary |  |  |  |

I/We are aware of the employment protection and working conditions legally in force in Ireland and the EU and operate our business accordingly (please tick)

| Yes | No |
| --- | --- |

Please enter categories of personnel currently employed (should total must recent year above)

| CATEGORY | NUMBERS |
| --- | --- |
| Engineers (Please provide CV’s GDPR protected) civil, electrical and /or Mechanical |  |
| Qualified Mechanical Personnel |  |
| Foreman |  |
| Apprentices |  |

NB. Without prejudice to the principle of equal treatment, SmartPly is not obliged to engage in a clarification process in respect of questionnaires with missing or incomplete information. Therefore, candidates are advised to ensure that they return FULLY COMPLETED questionnaires in order to avoid the risk of elimination from the competition.

NB. Without prejudice to the principle of equal treatment, SmartPly is not obliged to engage in a clarification process in respect of questionnaires with missing or incomplete information. Therefore, candidates are advised to ensure that they return FULLY COMPLETED questionnaires in order to avoid the risk of elimination from the competition.

Health and safety

Does your company have a Health and Safety Policy?	Yes (	No (

Please attached your REC certification or equivalent as an appendix                   Yes (	No (

Does your company have a written Safety Statement?	 Yes (	No (

Will your company comply with "all elements of Irish Law in relation to Health and Safety” Yes (	No (

If you have answered “No”, to either of the above, please explain why:

_______________________________________________

Have you been convicted under any aspect of Health and Safety legislation in the last five years?	Yes (	No (

Number of reportable accidents / incidents in the last 5 years?   __________

Who within your organisation is responsible for Health & Safety?

What qualification does he/she has in relation to H&S?

How many years is he or she qualified?

Title:  ____________________

Qualification:  ____________________

Name:___________________

Provide the following safety statistics (yearly) over the past 4 years. Statistics shall include contractors, subcontractors, or agency staff working under your control.

|  | 2020 | 2019 | 2018 | 2017 |
| --- | --- | --- | --- | --- |
| Fatalities |  |  |  |  |
| Lost Time Injuries (LTI) |  |  |  |  |
| Restricted Work Day Cases |  |  |  |  |
| Medical Treatments (MTC) |  |  |  |  |
| First Aids (FAC) |  |  |  |  |
| Near Misses (NM) |  |  |  |  |
| Number of hours worked |  |  |  |  |

## APPENDIX 4. Drawings and calculations

Documents:

383~210816~ Smartply Belview Surface Water Upgrade

383-403 – Settling tank inlet splitter arrangement

383-404 – Inlet pit screen

383-405 – Settling tank floating decanters

# Text boxes

Request for Tender for Site Surface Water Installation Upgrades at SmartPly Europe DAC

A1. CANDIDATE SUMMARY

Weighting: Pass/Fail only

Pass requirement:  Candidates must answer this section. If the candidate is a grouping, then a separate questionnaire must be completed for each group member.

A2.  FINANCIAL CAPACITY

Weighting: Pass/Fail only

Pass requirement:  Candidates must provide details of their turnover in respect of the previous two financial years. Alternatively, candidates must safisfy SmartPly that they have adequate financial capacity to deliver the services by alternative means. NOTE: in the case of the candidate being a grouping, this condition may be satisfied by the group members as a whole.

A3.  INSURANCES

Weighting: Pass/Fail only

Pass requirement:  Candidates must provide a statement from their insurers confirming that the candidate currently has in place the stated minimum levels of insurances or that such levels can be obtained if successful in the competition.

A4.  DECLARATION OF BONA FIDES

Weighting: Pass/Fail only

Pass requirement: Candidates must complete, sign and date this Declaration. Non-compliant candidates under any of the headings will be automatically disqualified.

A5.  TAX CLEARANCE CERTIFICATE

Weighting: Pass/Fail only

Pass requirement:  Candidates must provide evidence of a current and valid tax clearance certificate.

B1.  ULTIMATE PRICE

Maximum Points Available: 6,000

Minimum requirement to remain eligible in the competition: N/A

Candidates must provide a cost-effective proposal that covers all costs.

B2.  PREVIOUS EXPERIENCE

Maximum Points Available: 2,000

Minimum requirement to remain eligible in the competition:1,600

Candidates must provide details of at least 3 successfully executed projects of similar nature, scale and complexity to those to be carried out under this scope of works.

B3.  PROJECT PLAN

Maximum Points Available: 1,000

Minimum requirement to remain eligible in the competition: 600

Provision of Programme of work highlighting all Milestones in MS Project or similar. Installation schedule with manning levels – all resources identified and quantified

Please list the key milestones in Microsoft Project

Number of hours to execute the project

The total number of resources required

The tasks involved at each stage

Identify the critical path

B4.  HEALTH AND SAFETY (Policies and Procedures)

Maximum Points Available: 1,000

Minimum requirement to remain eligible in the competition:800

Candidates must have undertaken a course introducing the principles of the Safety, Health and Welfare at Work (Construction) Regulation’s amendment 2019 with regard to the service provider’s duties under those Regulations. Candidates must complete section B4 fully.