## ARP 1
Section No:
2 | Introduction
3 | Executive Summary
4 | Graphical Presentation of Data
7 | Health & Safety Issues
9 | Complaints Register
10 | Alarm Callouts & Site Incidents
16 | Equipment Calibration Records
19 | Waste & Sludge Disposal Records
20 | Analysis Results for Raw Influent, Settled Sewage & Mixed Liquor
22 | Analysis Results for Final Effluent

## ARP 4-3
Table of total daily flows for December 2022 MBR's |  |  |  | Outlet MBR 1 |  |  | Table of total daily flows for December 2022 MBR 2 |  |  | Outlet MBR 2
Date | MBR Flow #1 (m3) | MBR Flow #2 (m3) | Total Flow | Date | Readings | Flow | Date | Flow (m3) | Date | Readings | Flow
2022-12-01 | 1 | 6 | 7 | 2022-12-01 | 72033.8 | 1 | 2022-12-01 | 6 | 2022-12-01 | 52136.6 | 6
2022-12-02 | 1 | 6 | 7 | 2022-12-02 |  | 1 | 2022-12-02 | 6 | 2022-12-02 |  | 6
2022-12-03 | 2 | 6 | 8 | 2022-12-03 |  | 2 | 2022-12-03 | 6 | 2022-12-03 |  | 6
2022-12-04 | 2 | 6 | 8 | 2022-12-04 |  | 2 | 2022-12-04 | 6 | 2022-12-04 |  | 6
2022-12-05 | 1 | 12 | 13 | 2022-12-05 | 72039.5 | 1 | 2022-12-05 | 12 | 2022-12-05 | 52160.1 | 12
2022-12-06 | 2 | 12 | 14 | 2022-12-06 |  | 2 | 2022-12-06 | 12 | 2022-12-06 |  | 12
2022-12-07 | 4 | 5 | 9 | 2022-12-07 | 72043.4 | 4 | 2022-12-07 | 5 | 2022-12-07 | 52184 | 5
2022-12-08 | 3 | 5 | 8 | 2022-12-08 |  | 3 | 2022-12-08 | 5 | 2022-12-08 |  | 5
2022-12-09 | 3 | 4 | 7 | 2022-12-09 | 72049.9 | 3 | 2022-12-09 | 4 | 2022-12-09 | 52194.2 | 4
2022-12-10 | 3 | 4 | 7 | 2022-12-10 |  | 3 | 2022-12-10 | 4 | 2022-12-10 |  | 4
2022-12-11 | 4 | 5 | 9 | 2022-12-11 | 72056.3 | 4 | 2022-12-11 | 5 | 2022-12-11 | 52202.2 | 5
2022-12-12 | 3 | 5 | 8 | 2022-12-12 |  | 3 | 2022-12-12 | 5 | 2022-12-12 |  | 5
2022-12-13 | 3 | 5 | 8 | 2022-12-13 | 72062.8 | 3 | 2022-12-13 | 5 | 2022-12-13 | 52212.2 | 5
2022-12-14 | 2 | 4 | 6 | 2022-12-14 |  | 2 | 2022-12-14 | 4 | 2022-12-14 |  | 4
2022-12-15 | 2 | 5 | 7 | 2022-12-15 | 72068 | 2 | 2022-12-15 | 5 | 2022-12-15 | 52221 | 5
2022-12-16 | 2 | 5 | 7 | 2022-12-16 |  | 2 | 2022-12-16 | 5 | 2022-12-16 |  | 5
2022-12-17 | 3 | 4 | 7 | 2022-12-17 |  | 3 | 2022-12-17 | 4 | 2022-12-17 |  | 4
2022-12-18 | 2 | 5 | 7 | 2022-12-18 | 72074.8 | 2 | 2022-12-18 | 5 | 2022-12-18 | 52235.4 | 5
2022-12-19 | 2 | 5 | 7 | 2022-12-19 |  | 2 | 2022-12-19 | 5 | 2022-12-19 |  | 5
2022-12-20 | 3 | 6 | 9 | 2022-12-20 |  | 3 | 2022-12-20 | 6 | 2022-12-20 |  | 6
2022-12-21 | 6 | 3 | 9 | 2022-12-21 | 72082.2 | 6 | 2022-12-21 | 3 | 2022-12-21 | 52251.1 | 3
2022-12-22 | 5 | 3 | 8 | 2022-12-22 |  | 5 | 2022-12-22 | 3 | 2022-12-22 |  | 3
2022-12-23 | 3 | 3 | 6 | 2022-12-23 | 72092.7 | 3 | 2022-12-23 | 3 | 2022-12-23 | 52257 | 3
2022-12-24 | 3 | 3 | 6 | 2022-12-24 |  | 3 | 2022-12-24 | 3 | 2022-12-24 |  | 3
2022-12-25 | 2 | 3 | 5 | 2022-12-25 |  | 2 | 2022-12-25 | 3 | 2022-12-25 |  | 3
2022-12-26 | 3 | 4 | 7 | 2022-12-26 | 72100.5 | 3 | 2022-12-26 | 4 | 2022-12-26 | 52266.3 | 4
2022-12-27 | 3 | 3 | 6 | 2022-12-27 |  | 3 | 2022-12-27 | 3 | 2022-12-27 |  | 3
2022-12-28 | 3 | 11 | 14 | 2022-12-28 | 72106.7 | 3 | 2022-12-28 | 11 | 2022-12-28 | 52273.6 | 11
2022-12-29 | 4.6 | 5.8 | 10.4 | 2022-12-29 | 72109.7 | 4.6 | 2022-12-29 | 5.8 | 2022-12-29 | 52284.6 | 5.8
2022-12-30 | 5.7 | 15.6 | 21.3 | 2022-12-30 | 72114.3 | 5.7 | 2022-12-30 | 15.6 | 2022-12-30 | 52290.4 | 15.6
2022-12-31 | 3 | 6 | 9 | 2022-12-31 | 72120 | 3 | 2022-12-31 | 6 | 2022-12-31 | 52306 | 6
Average | 2.8806 | 5.6581 | 8.5387 | 2023-01-01 |  |  | Average | 5.6581 | 2023-01-01
Sum |  |  | 264.7 |  |  |  | Sum | 175.4
Formulas:
Date = [Date]
Date = [Date, row above]+1

## ARP 4-4
Table of Cumulative Hours Run
| 2022-12-01 | 2022-12-31 | Ave Daily Usage
Hours
Inlet screen | 33084 | 33125 | 1.4138
Inlet pump 1 | 4664 | 4672 | 0.27586
Inlet pump 2 | 5386 | 5393 | 0.24138
Balance tank 1,pump 1 | 7717 | 7723 | 0.2069
Balance tank 1,pump 2 | 7047.56 | 7051 | 0.11862
Anoxic mixer no. 1 | 4298 | 5017 | 24.7931
Anoxic mixer no. 2 | 59738 | 60437 | 24.1034
Membrane pump 1 (RAS) | 96965 | 97679 | 24.6207
Membrane pump 2 (RAS) | 56184 | 56899 | 24.6552
Sludge holding tank mixer | 4072 | 4072 | 0
Odour fan no. 1 | 59806 | 59806 | 0
Odour fan no. 2 | 77143 | 77862 | 24.7931
Forward feed no.1 | 10369 | 10369 | 0
Forward feed no.2 | 17418 | 17451 | 1.1379
Drainage pump | 1130 | 1131 | 0.034483
Balance tank 2, pump no.1 | 7166 | 7178 | 0.41379
Balance tank 2, pump no.2 | 16898 | 16898 | 0
Air Blower 1 | 20109 | 20109 | 0
Air Blower 2 | 62195 | 62914 | 24.7931
Air Blower 3 | 8591 | 9311 | 23.66
Air compressor | 22278 | 22997 | 24.7931
Ultraviolet system | 60978 | 60978 | 0

## ARP 6
Process and Operational Issues
Date | Description of Process Operational Issue | Implemented by
Nothing this month

## ARP 7-1
Site Safety Induction Report
Contractor Name |  |  | Contract Number
Date | Inductor | Inductee | Inductee Signature | Inductee Company
No Site Safety Inductions were undertaken during this monitoring period

## ARP 7-2
Site Staff Training Report
Trainee Name | Training Course | Trainer | Location | Course Duration | Start Date | Cost
Nothing to report

## ARP 7-3
Health & Safety Statistics Report
Plant Manager |  |  |  | Date | 2023-01-01
For Period | 2022-12-01
Site Involved | Cliffs of Moher WWTP
Category 1: Covers Fatalities and major Injuries
Category 2: Covers lost time accident resulting in more than 3 days absence
Category 3: Covers lost time accidents resulting in 3 days absence or less
Major Incident: Accident not covered by categories 1 to 3
Direct Employees
Number of Employees: |  | 1 | Exposure Hours: |  | 32hrs
| Category 1 | Category 2 | Category 3 | Major Incident | Near Miss
Number of Accidents | 0 | 0 | 0 | 0 | 0
Days lost
Direct Employees
Number of Employees: |  |  | Exposure Hours:
Subcontractors on Site
| Category 1 | Category 2 | Category 3 | Major Incident | Near Miss
Number of Accidents | 0 | 0 | 0 | 0 | 0
Days lost

## ARP 9
Complaints Register
Complainant's Name |  | Date
Nature of Complaint
Acknowledgement of Complaint | Author of Acknowledgement |  | Date Sent
Cause of Complaint
Action taken to Resolve cause of Complaint:
Final Outcome Report | Author of Final Outcome Report |  | Date Forwarded to Local Authority

## ARP 16
Equipment Calibration Record
Date | Equipment Description | Serial No. | Calibrated By (Name & Company) | Next Calib. Due | Calib. Cert Recd. | Comment
Nothing to report

## ARP 19-1
Non-Sludge Waste Disposal Record
Date | Waste Description | Amount removed | Removed By (Name & Company) | Destination Address | Receipt for Acceptance of Waste

## ARP 19-2
Outgoing Sludge Record
Batch No. | Date | Destination of Product | Type of Product | Quantity of Product | Contact at Destination
| 2022-12-06 | LMD | Sludge | 11

## MLSS
Analysis Results for Mixed Liquor (mg/l)
Date | MLSS MBR 1 | Anoxic 1 | MLSS MBR2 | Anoxic 2
06.12.2022 | 16948 | 16724 | 17332 | 15196
22.12.2023 | 16628 | 18456 | 18728 | 21204

## Influent
Analysis Results for Influent
Date | BOD (mg/l O2) | COD (mg/l O2) | SS (mg/l) | Total Nitrogen (mg/l) | Ammonia (mg/l) | Total Phosphorous (mg/l) | pH
2022-12-06 | 815.4 | 1675 | 1040 | 210 | 164.43 | 24.6 | 7.7
Maximum for month | 815.4 | 1675 | 1040 |  | 164.43 | 24.6 | 7.7
Average for month | 815.4 | 1675 | 1040 |  | 164.43 | 24.6 | 7.7
Design values | 220 |  | 170 |  | 105 | 11.2
| 3.7064 |  | 6.1176 |  |  | 2.1964
EPS USED TO PROVIDE RESULTS FOR TWO SAMPLES PER MONTH, BUT AS OF JULY 2010 THAT HAS CHANGED TO ONE SAMPLE PER MONTH

## Effluent
Analysis Results for Final Effluent
Date | BOD (mg/l O2) | COD (mg/l O2) | SS (mg/l) | Total Nitrogen (mg/l) | Ammonia (mg/l) | Total Phosphorous (mg/l) | pH | Date | BOD (mg/l O2) | COD (mg/l O2) | SS (mg/l) | Total Nitrogen (mg/l) | Ammonia (mg/l) | Total Phosphorous (mg/l) | pH
2022-12-14 | 1.4 | 92 | 5 | 10 | 0.11 | 1.7 | 8 | 2022-12-06 | 2.5 | 124 | 7 | 21 | 0.24 | 1.79 | 7.6
[8 empty] | 2022-12-14 | 1.4 | 92 | 5 | 10 | 0.11 | 1.7 | 8
Average for month | 1.4 | 92 | 5 | N/A | 0.11 | 1.7 | 8
Licence limit | 15 | 100 | 15 | 15 | 5 | 2 | 6 to 9
EPS USED TO PROVIDE RESULTS FOR TWO SAMPLES PER MONTH, BUT AS OF JULY 2010 THAT HAS CHANGED TO ONE SAMPLE PER MONTH

## Extra lab results
Extra Analysis Results for influent
Date | BOD (mg/l O2) | COD (mg/l O2) | SS (mg/l) | Ammonia (mg/l) | Total Nitrogen (mg/l) | Total Phosphorous (mg/l) | pH | FOGs (mg/l)
Design values | 220 |  | 170 | 105 |  | 11.2