23rd February 2024.

■■■■■■■■,

■■■■,

■■■■,

■■■■,

■■■■,

■■■■■■■■

Re:	Compliance with conditions attached to Section 4 Discharge Licence Reference WPL 11: Grant date 11th December, 1991.  Issued under Local Government (Water Pollution) Act 1977 (as amended).

--------------------------------------------------------------------------------------------------------------------------------------

A Chara,

Please find enclosed the results of the analysis of a recent sample taken from the outlet of the subject treatment plant to the stream on 13th February, 2024.  Copy of results enclosed for your records.

You will note that non-compliances were recorded for Suspended Solids with a result of 48 mg/l, where the licence limit is 10 mg/l and BOD with a result of 92 mg/l where the licence limit is 10 mg/l.

Based on these results you are required to examine the operation and performance of the treatment plant in question. A report is to be prepared and follow up testing undertaken to demonstrate that the issues have been identified and rectified. This report and test results are to be submitted to the undersigned within eight weeks of the date of this letter.

Please ensure to submit your own monitoring results as per the terms of your Discharge Licence. Results are to be forwarded to dischargelicences@wicklowcoco.ie or posted to the undersigned.

Please note that the submission of self-monitoring results will be receiving added attention from this date onwards.

If you have any query concerning the above you may contact pbrophy@wicklowcoco.ie or (0404) 20100.

Mise le meas,

_____________________

KIARA KAVANAGH

Senior Staff Officer

Planning, Development & Environment.

Encl: Results analysis sheet for 13th February 2024