19th January 2024.

■■■■■■■■,

■■■■,

■■■■,

■■■■,

■■■■,

■■■■■■■■

Re:	Compliance with conditions attached to Section 4 discharge licence reference WPL 11: Garden Village, grant date 11th December 1991 issued under Local Government (Water Pollution) Act 1977 (as amended).

-------------------------------------------------------------------------------------------------------------------------------

A Chara,

Thank you for your response of 10th January in the matter above. We have received the compliance monitoring results for 2023. It is noted that the effluent exceeded the limits in the discharge licence on five occasions and passed on one in 2023. In this regard the issues highlighted by Turbine on the age of the plant and the issue with storm water are noted. It is also noted that the missing 6 monitoring events from 2023 are being looked for with the contract lab.

It is noted from your monitoring data that phosphate in the effluent continues to remain low indicating the ferric dosing is working well, which will benefit the receiving water. However the limits of detection provided by the contract laboratory don’t provide enough resolution to ascertain the impact on the receiving water. In this regard you are requested to ensure compliance monitoring data in 2024 takes cognisance of the following:

- The limit in surface water regulations for ortho-phosphate is 0.035 mg/l as P, so any sample results up and downstream of the plant shall have a limit of detection of 0.02 mg/l or lower.

- The 2023 results did not include any Total Ammonia results. This is required in 2024 and the limit in the surface water regulations for Ammonia is 0.065 mg/l as N, so compliance data up and downstream of the plant shall have a limit of detection of 0.03 mg/l or lower.

- The Effluent and up and downstream monitoring results in 2024 shall include the parameter pH.

- The results shall be submitted within 1 month of the sample date, so compliance can be assessed on an ongoing basis.

With regards to the construction of a sewage pumping station and a connection to the public mains under the DPI Scheme, the council engineer dealing with this, Mark Costello, reports that the council is awaiting a response from Uisce Eirreann regarding prohibitive connection fees being sought, and the project cannot proceed until this issue is resolved.

Is mise le meas,

__________________________

KIARA KAVANAGH

Senior Staff Officer

Planning, Development & Environment.

Cc: Ken McAvoy 3C Project Services, 27 Westland Square, Pearse St, Dublin 2, D02 RW13.

CC: Brendan Fay at bfay@turbine.ie